## R1
MODBUS TO BACNET IP
Parameter | VFD-CON-PUMP3 | VFD-CON-PUMP2 | VFD-CON-PUMP1 | VFD-CHILL-PUMP1 | VFD-CHILL-PUMP2 | VFD-CHILL-PUMP3 | VFD-CHILL-PUMP4 | VFD-CHILL-PUMP5 | VFD-CHILL-PUMP6 | VFD-CHILL-PUMP7 | VFD-CHILL-PUMP8 | VFD-CHILL-PUMP9 | VFD-CHILL-PUMP10 | VFD-CHILL-PUMP11 | VFD-CHILL-PUMP12 | VFD-CHILL-PUMP13 | VFD-CHILL-PUMP14 | VFD-CHILL-PUMP15 | VFD-CHILL-PUMP16 | VFD-CHILL-PUMP17 | VFD-CHILL-PUMP18 | VFD-CHILL-PUMP19 | VFD-CHILL-PUMP20 | VFD-CHILL-PUMP21 | VFD-CHILL-PUMP22 | VFD-CHILL-PUMP23 | VFD-CHILL-PUMP24 | VFD-CHILL-PUMP25 | VFD-CHILL-PUMP26 | VFD-CHILL-PUMP27
Address | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
VFD-DCBUSVOLTAGE-MB(V) | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107 | 40107
VFD-SPEED-RPM-MB(Rpm) | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102 | 40102
VFD-FREQUENCY-MB(Hz) | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103 | 40103
VFD-AMPS-MB(A) | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104 | 40104
VFD-TORQUE-MB(%) | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105 | 40105
MOTOR POWER-MB(KW) | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106 | 40106
VFD-SPEED-DIR-MB | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101 | 40101
OUTPUT-VOLTAGE-MB(V) | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109 | 40109
VFD-TEMP-MB | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110 | 40110
VFD-KWH-MB(KWhr) | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115 | 40115
VFD-RUNTIME-MB(Hrs) | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114 | 40114
VFD-AI-PER (%) | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120 | 40120

## HostConfig
LOOP | R1
Device ID | 1 to 6
BAUDRATE | 9600
PARITY | EVEN
DATA BITS | 8
STOP BITS | 1
REG TYPE | Holding Register
Data Type | Integer Type